Results of testing ZWorld I/O Rack controller

Created:  2006-08-23  Mark Davis

Updated:  2006-09-18  Mark Davis

Here is what I have found so far in testing the new rack controller:

- Corrections needed to labeling on the circuit board:

- Digital Inputs:

"DI32" should read "DI27"

- Digital Outputs:

Current label:		Should read:

DO31			DO31

DO30			DO23

DO29			DO30

DO28			DO22

DO27			DO29

DO26			DO21

DO25			DO28

DO24			DO20

DO23			DO27

DO22			DO19

DO21			DO26

DO20			DO18

DO19			DO25

DO18			DO17

DO17			DO24

DO16			DO16

- Corrections needed to labeling on the schematic:

The order of the analog inputs on each connector is reversed (i.e. the lower # inputs are on pin 5, the higher # on pin 3 – e.g. AI00 is on pin 5, AI00 is on pin 3).

- Pin 15 is the only one on the read connectors that does not have a logical “pair”.  Pin 16 on each of the rear connectors should be +24V rather than ground (this would give pin 15 its own logical “partner”, like all the others have).

- Need to use the 574 variety of the octal latch for U46, U47, U48, U49

- The common connections next to the spare Digital Inputs should be +24V rather than ground.

- The common connections next to the spare Digital Outputs should be ground rather than +24V.

- The RS-232 connections on the back should be swapped so the one that shares a serial port with the RS-485 connection is next to the RS-485 connection.  The outlines around these ports should then be changed so the RS-232 and RS-485 connectors that share a port are in a group separate from the other RS-232 connector (which uses a separate serial port).  The point here is that there are 2 serial ports, not 3:  One is RS-232 only, the other is RS-232 OR RS-485.

- The D-sub 9 connector on the front and the ones on the back should female connectors rather than a male.  This indicates they are DCE (Data Communications Equipment) connections, as opposed to DTE (Data Terminal Equipment) connections.  Having said that, the one on the front ISN’T a standard RS-232 connection (plugging a serial line straight from the PC without the switch-box adapter in between will not work).  It would probably be a good idea to add the text “(NOT RS-232!)” under the current “DIAGNOSTIC PORT” label to help avoid problems in this regard.

- The logic on the Tx/Rx wiring for the RS-485 port is backwards on the schematic.  The correct wiring is as follows:

Male DB-25		J4

12		  5

11		  4

7		  3

5		  2

17		  1

16		10

3		  9

2		  8

14		  7