# Zworld/Rabbit-based NSCL controllers
Setup and Calibration

First Created:  2007-07-12  Mark Davis

Last Updated:  2009-06-05  Mark Davis

EE Document #: 111-0019-01-01_02*.doc

The following are quick-reference checklists for setting up a new controller or updating an existing controller.  For any step you are not familiar with, please refer to the detailed explanations following the checklist.  Also, this procedure applies only to newer controllers that are based on the DEBROS (Davis Embedded Baby Real-time Operating System) software base.  Please refer to the list of controllers at the end of this document if you are unsure if this process is the correct one to use.

# Setting up a Brand New Core Module:

The first section of the following process is normally needed only for a NEW controller.  Once a core module has the Download Manager installed, you can communicate with it over Ethernet using the Update Manager application from SHDesigns.  And if it has ANY working application boot image file on it, then you can update or replace the boot image file via a telnet connection.

The applications and files required for this process are located at:

\\exp\files\control\ctldev\Source\Embedded\Rabbit_ST\setup_tools

Installing the Download Manager (uses a serial connection and adapter box/cable):

- Connect a ZWorld PROG/DIAG Adapter Box to a serial port on your PC and to the DB-9 diagnostic connector on the controller (or directly to the Rabbit Core Module if necessary).

WARNING:  The female DB-9 connector on newer controllers is NOT an RS-232 port!  It is a TTL-level diagnostic/programming port, connected directly to the DIAG/PROG connector on the Rabbit Core module.  Do NOT connect a PC’s serial port directly to this port.  You MUST use a ZWorld PROG/DIAG Adapter box/cable to connect this port to a serial (RS-232) port on a PC!

- Set the DIAG/PROG switch on the adapter box to the PROG position.

- Use the Rabbit Field Utility (RFU.exe) to download the SHDesign’s Download Manager (DLM-III_D.bin) to the core module (this uses the serial connection and the PROG/DIAG Adapter Box).

- Once you have successfully downloaded the DLM file, exit the Rabbit Field Utility.

- Start a serial terminal connection (use the older FlashMenu script for now, option S off the main menu, or your favorite terminal emulator set to 115200 baud, 8 bits, no parity).

- Set the DIAG/PROG switch on the adapter box to DIAG position.  You should see the messages from the “Resident Download Manager” in your terminal window.

Downloading an application/boot-image file:

WARNING:  For the following steps, be CERTAIN you are selecting the new controller.  Selecting the wrong one and doing any of the following steps can cause a live controller to reboot!!!  The new controller will be the only one with “SHDesign’s Resident Download Manager” as the name and an IP address starting with “10”.

NOTE:  For the following steps, you must be using a PC that is configured with a 192.168.#.# address with a Subnet mask of 255.255.0.0 for its primary or secondary address.  You can check this using the command “ipconfig /all” in a command prompt window (Start / Run / “Cmd”).

- Set the Device ID switches to one of the reserved values (0xF0 – 0xFF: try 0xF8 first)

- Connect the core module to the control segment side of the NSCL Ethernet network.

- Start the Softool’s Update Manager (UpdateMGR.exe).  Click on the “Search for Devices” button to get a list of live controllers.

- Select the new controller (the one with the name “SHDesign’s Resident Download Manager” and an IP address starting with “10”).

- Use the “Change IP” button to change the IP address (this is a temporary change only, lost after rebooting).   Set the IP address to 192.168.250.#, where # is the decimal equivalent of the reserved Device ID you used above (0xF0-0xFF:  example: 0xF8 = 248, 0xF9 = 249, etc).

- Reselect the new device.  Be SURE you are selecting the one you just changed the IP address for.  WARNING: If you get a pop-up window with the message “This device is running user code”, then you have most likely selected the WRONG device!  If this happens, BE SURE to click on the NO button, or you will cause the controller to shutdown the application and run the Download Manager (effectively disabling the device the controller is connected to!!!!)

- Once you are sure you have the right device selected, click on the “Download” tab.

- Click on the “Add File” button.  In the dialog box that appears, make sure the “Compress File” option is NOT checked.

- Navigate to the following directory:   \\icarus\ctlrdata\release

- Select the .bin file for the type of controller you are working on and click “Open” (or simply double-click on the file to open it).  The file should download to the core module.

- Reset the controller to start the downloaded boot image/application file.  If you have a serial terminal running and connected, you should see the Download Manager restart and load the boot image you just downloaded.

- If you are not using one of the reserved Device ID’s, or the controller is not able to read the Device ID properly, you can use the serial terminal window to get a command prompt (just press enter) and use the “ifconfig” command to change the IP address (e.g. “ifconfig 192.168.125.150”).

# Updating an existing controller:

- If  you are updating a live controller (one connected to a part of the cyclotron), do NOT alter the ID switch settings.  If you are working on a controller on your bench, then change the Device ID switches to one of the reserved values (0xF0 – 0xFF).

- Open a Telnet connection to the controller.

If you are using one of the reserved Device ID switch settings, the IP address will be 192.168.250.#, where # is the decimal equivalent of the Device ID (0xF0=240, 0xF1=241, …, 0xFE=254, 0xFE=255).

If you are connecting to a live controller, then you can get the IP address from its control system record (the IPADDR field contains the address as a string).

If neither of these work, connect a ZWorld PROG/DIAG Adapter box to a serial port on your PC and to the DB-9 diagnostic connector on the controller (or directly to the Rabbit Core Module if necessary).   Start a serial terminal connection (use the older FlashMenu script for now, option S off the main menu, or your favorite terminal emulator set to 115200 baud, 8 bits, no parity).  Press enter until you get a command prompt, then type the command “ifconfig” to get the IP address the controller is using.

WARNING:  The female DB-9 connector on newer controllers is NOT an RS-232 port!  It is a TTL-level diagnostic/programming port, connected directly to the DIAG/PROG connector on the Rabbit Core module.  Do NOT connect a PC’s serial port directly to this port.  You MUST use a ZWorld PROG/DIAG Adapter box/cable to connect this port to a serial (RS-232) port on a PC!

- To see what boot image files are currently on the controller, type “bootimg”.  To download a new boot image file, use the “update” command.

Typing “update” by itself will simply update the primary boot image file. If you want to change to a different boot image, type “update newAppl.bin”, where “newAppl.bin” is the name of the boot image you want to download.

The update command also supports a “-r” option that causes the controller to reboot and load the new boot image file after it has finished downloading.

# How to do Calibrations

Two levels of calibration are required for most controllers:  Bench-top (controller-level) and Field (device-level).

The Bench-top calibration is done on the bench using precision voltage and/or current sources.  This process insures that all controllers of the same type produce consistent readings when given the same input.

Field (or device) calibration is done to allow any controller of the same type (that has valid bench-top calibration data) to be connected to a given device (or group of devices) and produce consistent readings.

Keeping these two calibrations separate is what allows us to swap controllers without recalibrating.  The older method used only a single level of calibration and required recalibrating whenever a controller was swapped.  This not only required much more time, but the opportunity to change the device settings and reboot control system servers to activate the new calibration data (often not practical when the system is live, which is when failures usually occur).

NOTE:  For the following steps, you must be using a PC that is configured with a 192.168.#.# address with a Subnet mask of 255.255.0.0 for its primary or secondary address.  You can check this using the command “ipconfig /all” in a command prompt window (Start / Run / “Cmd”).

! ! ! ! !  IMPORTANT  ! ! ! ! !

I cannot stress this enough:  Make sure you SAVE the results of the calibrations as instructed.  If you don’t save the result, the calibration data will be LOST when the controller is reset!  It would be like typing an entire document in Word without saving it and then hitting the reset button on your computer!

## Bench-top (controller-level) calibration

### Calibrating Analog Inputs:

- Establish 2 telnet connections to the controller.  Since this is a bench-top calibration, you can use one of the reserved Device ID settings to force a known IP address.  Just be sure that the one you select is not in use! (see the section on setting the device ID for details).

- In the 1st telnet window, type the command “ios” (for Input/Output State).  This shows the state of all the analog and digital inputs and outputs.

- Press the letter ‘A’ to change to Analog-only mode, with labels for each signal.

- In the 2nd telnet window, type the command “adccalib show”.  This will show you the existing calibration data for the analog inputs with a name for each.

- To calibrate all the analog inputs, type the command “adccalib all”.  To calibrate a single input specify the name for the input rather than “all”.  If you want to calibrate a group of inputs with common names, you can specify the part of the name that is common to all of them.

- For each input in the group you selected in the last command, you will be prompted twice.  In each case, you need to connect your current or voltage source to the specified input and either set it to the default value given in the prompt, or type the value that it IS set to if different than the default.

- After the 2nd prompt for each input, the calculated gain and offset (and the range of values the input can handle) are displayed.  Look at these values and make sure they look reasonable.  Also, the value shown in your 1st telnet window (the one running “ios”) should now show the value your input source is providing.

If the offset, gain, or range values do not look correct, or the value shown by ios for the input is not correct, you can either abort the calibration process and start again, and make a note that you need to redo that input later (or fix it if it is not working correctly).

- Once you have completed calibrating all the inputs in a group, you will be prompted to save the results.  DO SO!

- Once the calibrations are complete, and you have saved them there should be a file on the controller named “hdwcfg”.  You can verify this with the ls or dir command.  Check the date and time on this file and make sure it shows the current date and time!

- The last step is to copy the calibration file to a remote server.  Since the file name on the controller is the same for all controllers, and is independent of the device the controller will be connected to, you need to add a suffix to the name when copying it.  For consistency, please use the following format:

hdwcfg_type_serialnum

where “type” is the controller type (e.g. ps8rack) and “serialnum” is the serial # assigned to board in the controller that has the ADC and DAC chips on it (which is NOT the ZWorld core module!  Do NOT use the Core Module ID!!!)

Once you have determined the name for the remote copy of the file, write the name on the circuit board (NOT the core module) using a thin permanent marker, and use the “cp” command to copy it to the remote server like this:

cp hdwcfg /srfs/hdwcfg_type_serialnum

Example for a ps8rack controller with serial # SN0001

cp hdwcfg /srfs/hdwcfg_ps8rack_SN0001

And always remember:  SAVE!!!  SAVE!!!  SAVE!!!  SAVE!!!

(Don’t go through this entire process and then turn off the power or bump the reset button!!!)

IMPORTANT NOTE:  You can save the currently in-use calibration values at any time by typing the command “save all” a command-line prompt.  Opening a 3rd telnet window and doing this after each input is calibrated is not a bad idea, especially if the reset button on the controller is in an accessible place where you might bump it!  Note also that you can use the up and down arrows to very easily repeat recent commands.

### Calibrating Analog Outputs

  - Establish 2 telnet connections to the controller.  Since this is a bench-top calibration, you can use one of the reserved Device ID settings to force a known IP address.  Just be sure that the one you select is not in use! (see the section on setting the device ID for details).

  - In the 1st telnet window, type the command “ios” (for Input/Output State).  This shows the state of all the analog and digital inputs and outputs.

  - Press the letter ‘A’ to change to Analog-only mode, with labels for each signal.

  - In the 2nd telnet window, type the command “daccalib show”.  This will show you the existing calibration data for the analog outputs with a name for each.

  - To calibrate all of the analog outputs, type the command “daccalib all”.  To calibrate a single output specify the name for the output rather than “all”.  If you want to calibrate a group of outputs with common names, you can specify the part of the name that is common to all of them.

  - Calibrating an analog output requires that the output be set to 2 different values reasonably close to the ends of its possible range.  Normally the default values used by the calibration process do a good job, but if you need to use different values for any reason, you can open a 3rd telnet window and use the “dac” command to force a different value.

  - For each output in the group you selected in the daccalib command, you will be prompted twice.  For each prompt, you need to measure the output current or voltage being produced at the specified output and enter it at the prompt.

  - After the 2nd prompt for each output, the calculated gain and offset (and the range of values the output can produce) are displayed.  Look at these values and make sure they look reasonable.

  - Once you have completed calibrating all the outputs in a group, you will be prompted to save the results.  DO SO!

  - Once the calibrations are complete, and you have saved them there should be a file on the controller named “hdwcfg”.  You can verify this with the ls or dir command.  Check the date and time on this file and make sure it shows the current date and time!

- The last step is to copy the calibration file to a remote server.  Since the file name on the controller is the same for all controllers, and is independent of the device the controller will be connected to, you need to add a suffix to the name when copying it.  For consistency, please use the following format:

hdwcfg_type_serialnum

where “type” is the controller type (e.g. ps8rack) and “serialnum” is the serial # assigned to board in the controller that has the ADC and DAC chips on it (which is NOT the ZWorld core module!  Do NOT use the Core Module ID!!!)

Once you have determined the name for the remote copy of the file, write the name on the circuit board (NOT the core module) using a thin permanent marker, and use the “cp” command to copy it to the remote server like this:

cp hdwcfg /srfs/hdwcfg_type_serialnum

Example for a ps8rack controller with serial # SN0001

cp hdwcfg /srfs/hdwcfg_ps8rack_SN0001

And always remember:  SAVE!!!  SAVE!!!  SAVE!!!  SAVE!!!

(Don’t go through this entire process and then turn off the power or bump the reset button!!!)

IMPORTANT NOTE:  You can save the currently in-use calibration values at any time by typing the command “save all” a command-line prompt.  Opening a 3rd telnet window and doing this after each output is calibrated is not a bad idea, especially if the reset button on the controller is in an accessible place where you might bump it!  Note also that you can use the up and down arrows to very easily repeat recent commands).

## Field (device-level) calibration:

Field, or device-level, calibration provides the information necessary to convert between the voltage and current levels required by an actual device or group of devices and the engineering units readings and settings are expressed in.

WARNING:  This process must ONLY be done using a controller that has been bench calibrated first!  Performing a device-level calibration with a controller that has NOT been bench calibrated will result in calibration data that will work only with the controller the calibration was done with.

### Calibrating Device Readings:

- Make sure the controller you are using has been bench calibrated.  At the very least, use the commands “adccalib show” and “daccalib show” to check the ADC and DAC calibration data.  If the gains and offsets are all the same, then the controller has NOT been bench calibrated!

- Make sure the Device ID switches are set to match the DEVID field in the EPICS record for the device.  Remember that the switches are either a binary (base-2) or hexadecimal (base-16) representation of the Device ID.  If you use a control system application (like QtChan or Chart Recorder or Param101) to get the value of the DEVID field for a record it will be shown in decimal and will have to be converted (you can use the calculator application in windows to do this:  Just set the “View” to “Scientific” mode, click on the radio button for the format you have it in, enter the id, then click on the radio button for the format you need it in).

- Establish 2 telnet connections to the controller.

- In the 1st telnet window, type the command “state”.  This shows the state of the controller, which should include values for all the readings and settings in engineering units.

- In the 2nd telnet window, type the command “readcalib show”.  This will show you the existing device-level read-back calibration data for the inputs with a name for each.

- Calibrating a reading requires 2 different test-points reasonably close to the ends of its possible range.  Since it is the device that is producing the values we are calibrating to, you will need to apply whatever settings are required to achieve these 2 different read-back values.  This is normally done using the control system interface for the device.  For example, on a power supply controller, you would most likely change the current or voltage set-point.

If the control system interface is not available for some reason, another option is to open a 3rd telnet window and use it to directly view and set register values (the control system currently communicates with the controls via a ModBus/TCP connection to read and set “registers” that represent variables in the program logic).

The command “reg” will show all the registers and their values.  “reg str” will show all registers containing the string “str” in their name.  And “reg name value” will change the value of the named register to the given value.

Examples:  (NOTE: names are NOT case sensitive)

reg amp  - show all registers with the string “amp” in their name

reg ampset 12.3  - sets the value of the register “ampSet” to 12.3

- Determine which input you want to calibrate and type the command “readcalib name”, where name is the name shown for the input by the readcalib show command.

- Apply settings to the device as required to produce a reading for the selected input that is close to the lower end of its range.  For example, on a power supply controller with a range of 0 to 100 amps, use a value of 5 or 10 amps.

- Determine the actual value the reading should show in engineering units by making whatever measurements and applying whatever calculations are necessary.  Enter the value at the prompt for the 1st test point.  For example, if a 100 amp supply produces a voltage of 0 for 0 amps and 10 for 100 amps, then a reading of 1 volt would mean an actual current of 10 amps.

- Apply settings to the device to achieve a reading close to the higher end of the range.  Determine the actual value in engineering units and enter that value at the prompt for the 2nd test point.

- After the 2nd prompt for each input, the calculated gain and offset (and the range of values the input can handle) are displayed.  Look at these values and make sure they look reasonable.

- Once you have verified that an input is properly calibrated, be sure to answer “Y” when prompted to save the calibration data.

- Once the calibrations are complete, and you have saved them there should be a file on the controller with the current date and time, and a name of the format “##_####_devData”, where ## is the controller type expressed as 2 hexidecimal digits, and #### is the Device ID the controller is set to.  You can check this using the ls or dir command.

- Type the command “syslog” at a command prompt.  Within 60 seconds you should see an entry something like the one below indicating the file has been backed up to the remote server:

2007-07-18 13:20:10 backupd[6]: update backup copy: /srfs/PS8_xF2_devData

2007-07-18 13:20:10 backupd[6]:   local:  Wed Jul 18 13:19:57 2007

2007-07-18 13:20:10 backupd[6]:   remote: Tue Jan  2 02:28:16 2007

- Once the file has been backed up, it is safe to reset or turn off power to the controller.

### Calibrating Device Settings:

- Make sure the controller you are using has been bench calibrated.  At the very least, use the commands “adccalib show” and “daccalib show” to check the ADC and DAC calibration data.  If the gains and offsets are all the same, then the controller has NOT been bench calibrated!

- Make sure the Device ID switches are set to match the DEVID field in the EPICS record for the device.  Remember that the switches are either a binary (base-2) or hexadecimal (base-16) representation of the Device ID.  If you use a control system application (like QtChan or Chart Recorder or Param101) to get the value of the DEVID field for a record it will be shown in decimal and will have to be converted (you can use the calculator application in windows to do this:  Just set the “View” to “Scientific” mode, click on the radio button for the format you have it in, enter the id, then click on the radio button for the format you need it in).

- Establish 2 telnet connections to the controller.

- In the 1st telnet window, type the command “state”.  This shows the state of the controller, which should include values for all the readings and settings in engineering units.

- In the 2nd telnet window, type the command “setcalib show”.  This will show you the existing device-level settings calibration data for the outputs with a name for each.

- Calibrating a setting requires 2 different test-points reasonably close to the ends of its possible range.  Since it is the device itself that reacts to these settings, you will need to apply whatever set-points are required to achieve these 2 different states.  This is normally done using the control system interface for the device.  For example, on a power supply controller, you would most likely change the current or voltage set-point.

If the control system interface is not available for some reason, another option is to open a 3rd telnet window and use it to directly view and set register values (the control system currently communicates with the controls via a ModBus/TCP connection to read and set “registers” that represent variables in the program logic).

The command “reg” will show all the registers and their values.  “reg str” will show all registers containing the string “str” in their name.  And “reg name value” will change the value of the named register to the given value.

Examples:  (NOTE: names are NOT case sensitive)

reg amp  - show all registers with the string “amp” in their name

reg ampset 12.3  - sets the value of the register “ampSet” to 12.3

- Determine which setting you want to calibrate and type the command “setcalib name”, where name is the name shown for the output by the setcalib show command.

- Apply settings to the device as required to produce a value for the selected output that is close to the lower end of its range.  For example, on a power supply controller with a range of 0 to 100 amps, use a value of 5 or 10 amps.

- Determine the actual value the setting results in (in engineering units) by making whatever measurements and applying whatever calculations are necessary.  Enter the value at the prompt for the 1st test point.  For example, if you are calibrating the set-point for a 100 amp supply, and a setting of 10 produces an actual output of 9.8 amps, then 9.8 is what you would enter at the prompt.  NOTE that, if you have already calibrated the readings, then you can often use the value shown for the associated reading.

- Apply settings to the device to produce a value for the output that is close to the higher end of the range.  Determine the actual value in engineering units and enter that value at the prompt for the 2nd test point.

- After the 2nd prompt for each input, the calculated gain and offset (and the range of values the output can achieve) are displayed.  Look at these values and make sure they look reasonable.

- Once you have verified that an output is properly calibrated, be sure to answer “Y” when prompted to save the calibration data.

- Once the calibrations are complete, and you have saved them there should be a file on the controller with the current date and time, and a name of the format “##_####_devData”, where ## is the controller type expressed as 2 hexidecimal digits, and #### is the Device ID the controller is set to.  You can check this using the ls or dir command.

- Type the command “syslog” at a command prompt.  Within 60 seconds you should see an entry something like the one below indicating the file has been backed up to the remote server:

2007-07-18 13:20:10 backupd[6]: update backup copy: /srfs/2F_00F2_devData

2007-07-18 13:20:10 backupd[6]:   local:  Wed Jul 18 13:19:57 2007

2007-07-18 13:20:10 backupd[6]:   remote: Tue Jan  2 02:28:16 2007

- Once the file has been backed up, it is safe to reset or turn off power to the controller.

# Setting the Device ID:

Each controller has a set of DEVICE ID switches that tells the controller what device (or set of devices) the controller is connected to.  These switches usually come in one of two formats:  8 individual slide or flip switches housed in a 16-pin DIP format, or two Hexadecimal thumbwheel switches.

The Device ID for a controller is normally expressed in Hexadecimal format (e.g. 0xF8).  In the case of the 8 individual switches, the first 4 switches make up the first Hex digit while the 2nd 4 make up the 2nd Hex digit (e.g. 0xF8 = 1111-1000, where 1 is usually the ON position).

All ID’s with the left/most significant digit of “F” (0xF0- 0xFF) are reserved for setup and diagnostic purposes.  These addresses are special in that the software will force the controller to use one of the reserved IP addresses whenever the ID is set to one of these reserved values.  The address used in this case is 192.168.250.xxx, where xxx is the decimal equivalent of the Device ID itself (i.e. 0xF0 == 240, 0xFF = 255).  The following table shows the IP address used for each of the reserved device ID’s.

| ID | IP Address |
| --- | --- |
| 0xF0 | 192.168.250.240 |
| 0xF1 | 192.168.250.241 |
| 0xF2 | 192.168.250.242 |
| 0xF3 | 192.168.250.243 |
| 0xF4 | 192.168.250.244 |
| 0xF5 | 192.168.250.245 |
| 0xF6 | 192.168.250.246 |
| 0xF7 | 192.168.250.247 |
| 0xF8 | 192.168.250.248 |
| 0xF9 | 192.168.250.249 |
| 0xFA | 192.168.250.250 |
| 0xFB | 192.168.250.251 |
| 0xFC | 192.168.250.252 |
| 0xFD | 192.168.250.253 |
| 0xFE | 192.168.250.254 |
| 0xFF* | 192.168.250.255* |

*  Note that the 0xFF setting results in a last byte of 255, which is usually treated as a broadcast address, making this setting unusable in most cases.

When setting up a new device, please try the ID 0xF8 (1111-1000) first .

# Connect your PC to the Core Module:

If the controller is one with a female DB-9 “DIAGNOSTIC PORT” connector, then plug the male DB-9 connector closest to the end of the PROG/DIAG adapter cable in to the female DB-9 “DIAGNOSTIC PORT” on the controller.

If the controller does NOT have such a connector, then connect directly to the core module by plugging the 10-pin connector at the end of the ribbon cable directly in to the core module, making sure that pin 1 (the side with the red wire) is closest to the edge of the core module.

# ZWorld/Rabbit Controller List

## Newer controllers (using Softools C compiler and DEBROS)

| Name | Type # | Description |
| --- | --- | --- |
| ECROven | 0x2D | Controls a group of supplies for the ECR Oven |
| PhaseCtlr | 0x2F | Digital RF Phase Controller |
| RFMonitor | 0x31 | RF Monitor (simply monitors varies RF signals) |
| PS8Rack | 0x50 | Controls up to 8 independent power supplies |
| ModularPS | 0x51 | Controls up to 10 interdependent power supplies |
| DVR | 0x52 | Dee Voltage Regulator – regulates RF Cavity Voltage |
| SparkDetector | 0x53 | Module to detect and count sparks in the RF system |
| TCPS | 0x54 | Newer version of code for Trim Coil Power Supplies |
| LLRFTurnOn | 0x55 | Low-Level RF Turn-On module |
| Starter | 0xF8 | Generic program for testing controllers |

## Older style controllers (using Dynamic-C compiler and no OS)

| Name | Type # | Description |
| --- | --- | --- |
| BCM_RR | 0x09 | Beam Current Monitor (Reed-Relay version) |
| BBServo | 0x14 | Bang-Bang Servo motor controller |
| BCM_SS | 0x19 | Beam Current Monitor (Solid-State relay version) |
| DCServo | 0x1B | DC Servo motor controller |
| RFPhase | 0x20 | Analog RF Phase monitor/controller |
| FastRFOff | 0x21 | Fast RF Off (uses PLC chip to quickly disable things when needed) |
| RFServo | 0x2B | RF Servo controller (monitor RF and control BB or DC servo motor) |
| MWaveAmp | 0x2C | Microwave Amplifier |
| RevSwitch | 0x2E | Reversing Switch power supply controller |
| TCPS | 0x30 | Trim Coil Power Supply controller |