Power Supply-8 Rack (PS8Rack) Controller

Software Requirements

National Superconducting Cyclotron Laboratory, MSU

## Created:  Mark Davis, 10/27/2006      Last Updated:  Mark Davis, 12/07/2007

##### EE Document #: 038-0048-01-01_00.doc

# Introduction

The NSCL PS8Rack controller is a rack-mounted device used to monitor and control 8 independent analog power supplies.  Advantages over the previous method (separate analog and digital I/O boards in VME crates) include reduced cost, a reduction in the number of supplies affected by a single-point failure, shorter connections between the power supplies and the controlling device (reducing noise), and the ability to alter calibrations on-the-fly.

Basic functional capabilities:

- Support for both unipolar and bipolar supplies.

- Automatically detect whether a unipolar or bipolar supply is connected to each port and adjust behavior accordingly.

- Periodically check the state of the inputs for each supply and update the state of the output signals as needed.

- Remote control and monitoring via ethernet connection

- Controller and Device-specific configuration and calibration information stored in a small file system on the controller, with backup copies kept on a remote server.  A unique ID is assigned to the device (or group of devices) managed by a controller, allowing a new controller to be swapped for an existing one and configure itself from the backup copy of the Device-specific information stored by the older controller.  For details, see the latest version of the following EE department documents:

  - Automatic Controller Configuration: 111-0016-01-01_##.doc

  - Setup and Calibration: 111-019-01-01_##.doc

Functional overview:

The controller has 8 independent connections with the same number and type of I/O signals.

Differences in the external wiring for unipolar and bipolar supplies allows the controller to automatically determine which type of supply is connected to each port, but only when the supply is turned off.

Control and monitoring of the supplies is done using a combination of digital and analog I/O signals.

The controller contains two independent serial ports (one RS-232 only and one RS-232/RS-485) that could be used in the future to communicate with supplies with serial interfaces.

The control logic for bipolar supplies is fairly straightforward.  It turns the supply on or off in response to commands and interlocks, sets the analog output to control the output current, and monitors the state of the supply.  Any special handling of a change in the polarity of the setpoint is handled by the supply itself.

For unipolar supplies, the controller is also responsible for specifying which way current should flow through the load and changing it as needed in a safe manner (i.e. insuring the supply is off before changing the direction).

Configurable Engineering parameters:

These are values that are normally configured when a controller is installed and tested with a new set of power supplies.  The software-configurable values are included in the Device-specific values stored in a file on the controller (with backup copies on a remote server).

Modification of the following parameters (both hardware and software) should be limited to engineering staff with knowledge on how to properly configure them.

Software Settings:

- Gain and offset for each of the analog inputs and outputs:  A table of values used to convert between engineering units and analog input and output values.  Set using firmware calibration commands while the equipment is in operation.

- Minimum and maximum current settings for each power supply.

Hardware Settings:

- Device ID switches:  Must be set to the ID assigned to the device(s).   Used by the control system to locate and configure controllers, and by controllers when saving or restoring configuration data.

###### Inputs and Outputs, Operating Parameters

# Software Inputs/Settings

- On/Off

- Current set-point

- Reset Interlock

# Software Outputs/Readings

- Current value of all software inputs/settings

- Current operating state

- Output voltage and current

- State of interlock(s)

### Hardware Inputs

- External Interlock

- Power Supply Interlock (when available)

- Supply On/Off (for bipolar supplies).  Also used for determining the type of supply connected (see description under Theory of Operation for details)

- Output voltage reading

- Output current reading

#### Hardware Outputs

- On/Off command

- Reset (for bipolar supplies) or Polarity (for unipolar supplies).  Also used for determining the type of supply connected (see description under Theory of Operation for details)

# Theory of Operation

Bipolar supplies connected to this controller are expected to handle a positive and negative control voltage and handle all aspects of changes in polarity themselves.

Unipolar supplies require an external polarity switch and are set to zero and shut off before changing the state of the polarity switch.

To allow the controller to determine whether a unipolar or bipolar supply is connected to a port, the wiring for a unipolar supply connects one of the digital outputs to one of the digital inputs to produce a behavior that is different than what occurs when a bipolar supply is connected.

The digital output used is the one that provides the reset signal for bipolar supplies and controls the external polarity switch for unipolar supplies.  The digital input used is the one providing the on/off status for bipolar supplies, which is (otherwise) not used for unipolar supplies.

The controller can use this configuration to detect the supply type by briefly pulsing the digital output and observing the state of the digital input before, during, and after the pulse.  For bipolar supplies, the output is a reset command to the power supply, and the input is the supply on/off status, so the digital input will not follow the state of output.  For unipolar supplies, the output is connected directly to the input, so if the state of the input follows the state of the output, the wiring is for a unipolar supply.

Because the digital output used is the reset pulse for bipolar supplies and the polarity control for unipolar supplies, this test must be limited to when the supply is turned off.

For unipolar supplies, the digital input used to monitor the interlock state of the power supply is tied high (indicating no interlock condition from the supply).  By restricting reset pulses for bipolar supplies to when this input is low (indicating the supply needs to be reset), we also avoid the possibility of accidentally changing the polarity for a unipolar supply when we thought we were sending a reset pulse to a bipolar supply.

The fact that the Power Supply Interlock status input is always held high by the wiring for a unipolar supply is another condition that should be used when testing which kind of supply is connected.

# Operational Logic

- Real-Time main application process that runs at the highest priority:

  - Handles all application-specific initialization and then runs a continuous loop.

  - The loop is executed every 10ms and runs from start to finish with minimal interruptions

  - At the end of the loop, the process blocks until the start of the next 10ms interval, at which time it is resumed with minimal latency to execute the loop and block again.  The 10ms scheduler timing is quite accurate and is not affected by any delays in the application itself.

  - All values for which the application logic needs to track “single-step” changes (a change between consecutive iterations of the logic loop) are kept in a structure named ApplState.  3 instances of this structure (prev, cur, next) are kept at all times.

  - The loop logic contains the following basic phases:

    - Read the current state of all hardware input signals

    - Update the state of the hardware output signals using “next”

    - Set prev = cur, then cur = next

    - Update values in “cur” using only “prev” and the just-read inputs

    - Update values in “next” using only “prev” and “cur” values

  - Updating the state of the controller takes in to account the following:

    - The current state of the hardware inputs and outputs

    - The current logic state of the controller

    - Requests to change the state of the controller (implied by the current state of the hardware, or received from an external client via a communications channel).

Any changes to the desired state of the hardwired output signals are applied at the beginning of the next interval, just after reading the inputs.

The following logic is applied to each of the 8 power supplies independent of the state of the other supplies:

- Whenever the Supply On/Off output is not asserted, the controller will frequently test for the type of supply connected by pulsing Polarity/Reset output and the observing the effect on the Supply On/Off input.  If the Supply On/Off input follows the state of the pulses, and the Power Supply Interlock input never indicates an interlock, then the supply type is assumed to be unipolar (see Theory of Operation for details).

- A Reset command is ignored unless the Power Supply Interlock input indicates the supply needs to be reset.  The wiring for a unipolar supply ties the Power Interlock Status high (indicating no interlock), so this is a simple safeguard that avoids the possibility of sending inappropriate polarity change commands when a unipolar supply is connected.

- When a new setpoint requiring a change in polarity is received for a unipolar supply, the following process is followed before applying the new setpoint:

  - Set active setpoint to 0

  - Wait until the supply output drops close to zero

  - Turn the supply off

  - Change the state of the polarity control bit

  - Wait a short (configurable) period to give the PLC controlling the polarity switch time to react

  - Turn the supply on

  - Apply the new setpoint

- Turning the controller Off or pressing the Reset button will cause the Power Supply ON output to be disabled.  After a Reset or a loss of power, the controller will NOT (re)assert the ON output until it is commanded to do so from an outside source.  The controller NEVER attempts to restore the state of the outputs to the state they were in before a reset or power loss.

- An active (asserted) state on the External Interlock will disable the ON output independent of the controller logic.  The controller must NOT be able to turn on the Power Supply while the External Interlock is asserted.

- The controller periodically reads the state of the analog and digital inputs and updates the following values:

  - The existing Voltage and Current output

  - Actual On/Off state (for bipolar supplies)

  - Interlock condition asserted by the Power Supply (for bipolar supplies)

  - Interlock condition asserted by an External Source (normally a PLC that monitors several conditions related to the operation of the Power Supply)

- Accept, process, and respond to queries and commands from external sources (typically read via ModBus protocol connections over ethernet).  The commands are typically expressed as changes to values in ModBus registers, and include the following:

  - Supply Set Point:  Alter the voltage that controls the output of the supply

  - Supply On/Off:  Enable or Disable the power supply

  - Reset Supply:  Attempt to clear a Power Supply Interlock state (clearing of any external interlock is handled by the control system layer)

- The ACTIVITY LED is on the outside of the box, and is used to check the overall state of the controller.  Normally the LED blinks at approximately 8 Hz.  Slower or varied blink rates may be used to indicate problems or special operating conditions.