NSCL Dee Voltage Regulator (DVR)

Software Requirements

National Superconducting Cyclotron Laboratory, MSU

## Created:  Mark Davis, 11/28/2007      Last Updated:  Mark Davis, 05/27/2007

EE Document #: 045-0071-01-01_01.doc

# Introduction

The NSCL DVR is a double-wide NIM module used to control the RF amplitude in a resonator or cavity.  The module receives an analog feedback voltage that it properly scales and then uses it in an analog feedback loop to precisely (1:10E+4) regulate the resonator or cavity voltage.

Basic functional capabilities:

- Remote control and monitoring via ethernet connection

- Monitors RF ON/OFF state and adjusts the analog setpoint for the feedback loop to efficiently start and ramp the cavity voltage.

- Accepts front panel commands and updates front panel displays.

- Controller and Device-specific configuration and calibration information stored in a small file system on the controller, with backup copies kept on a remote server.  A unique ID is assigned to the device (or group of devices) managed by a controller, allowing a new controller to be swapped for an existing one and configure itself from the backup copy of the Device-specific information stored by the older controller.  For details, see the latest version of the following EE department documents:

  - Automatic Controller Configuration: 111-0016-01-01_##.doc

  - Setup and Calibration:  111-019-01-01_##.doc

Functional overview:

This controller functions predominantly as a remote control interface with a few additional features.

The primary function of the controller is to monitor the ON/OFF status of the RF via a digital input and maintain the cavity voltage at one of two setpoints:  One for the OFF or INITIAL/cold state, and one for the ON or FINAL/warm state.

Regulation of the cavity voltage is done by an analog feedback loop using a setpoint voltage supplied by the control logic.  As long as the module has power, one of the two setpoints (or a value in between) is applied to the feedback loop.

To avoid surges due to unmatched conditions, particularly when the RF is first turned on and still warming up, configurable delays and ramp rates are used to gradually ramp the setpoint from one value to another.

The front panel contains a knob, a digital meter, and switches for viewing the current operating voltage and making changes to the setpoints.  These values and all the other software configurable parameters can also be viewed and/or set via the control system software interface.

Configurable Engineering parameters:

Configurable Engineering parameters are those that are generally set and then left alone for normal operation.

Modification of these parameters (both hardware and software) should be limited to engineering staff with knowledge on how to properly configure them.

Software Settings:

- Gain and offset for each of the analog inputs and outputs

- ON Delay:  The # of seconds to wait after the RF changes from OFF to ON before the active setpoint begins ramping toward the RF-ON Setpoint.

- Cold Ramp Rate:  The rate at which the active setpoint is ramped toward the RF-ON Setpoint after the ON Delay has been observed.

- Warm Ramp Rate:  The rate at which the active setpoint is ramped toward a new RF-ON Setpoint after the ON Delay has expired and the active setpoint has reached the previous RF-ON Setpoint.

- Limiter Error:  The maximum magnitude for the Limiter voltage that is not considered an error.

- Regulation Error:  The maximum difference between the active setpoint and the cavity voltage readback that is not considered an error.

- Knob Rate:  A scaling factor for applying knob movement to one of the setpoints.

- RF-OFF Setpoint:  INITIAL or cold setpoint

Hardware Settings:

- Device ID switches:  Must be set to the ID assigned to the device(s).   Used by the control system to locate and configure controllers, and by controllers when saving or restoring configuration data.

- Attentuator (thumbwheel switches on front panel):  Sets the gain for the Peak Detector Input, from which the RF Cavity Voltage is derived.

- Hardware Configuration Header:  A 16-pin DIP head with resistors and capacitors that sets gains for the analog I/O and the feedback regulation loop.  One of the resistors is used to provide a fixed voltage read by the controller indicating which of 8 possible header configurations is in use.

Inputs, Outputs, and Operating Parameters

# Software Inputs/Settings

- RF-ON Setpoint:  FINAL or warm setpoint

# Software Outputs/Readings

- Current value of all software settings and hardware inputs/outputs

- Active Setpoint:  The value currently in effect for the feedback control loop circuit.

- Ramp Mode:  Keeps track of the mode currently in effect for making adjustments to the Active Setpoint.

### Hardware Inputs

- Open/Closed loop switch position

- FINAL push-button position

- INITIAL push-button position

- RF ON/OFF

- Local/Remote switch position

- RF Cavity Voltage (derived from Peak Detector Input and FP Attenuator settings)

- External analog limit level

- Hardware Configuration indicator

- Front Panel Encoder/Knob pulses

- CPU Reset button

#### Hardware Outputs

- Limited LED

- Error LED

- Setpoint for RF Cavity voltage regulator circuit

- FP Meter

- CPU activity LED

# Theory of Operation

The two main features of the module are an analog feedback loop that controls the RF cavity voltage, and an embedded SBC (Single Board Computer) whose primary tasks are to provide the setpoint for the feedback loop and monitor the RF cavity voltage and ON/OFF status.

The controller maintains two setpoints:  RF-OFF Setpoint (INITIAL/cold) and RF-ON Setpoint (FINAL/warm).   These setpoints and the RF ON status determine the Active Setpoint applied to the feedback loop as follows:

Prior to (1):  Whenever the RF is OFF, the Active Setpoint is set to the RF-OFF Setpoint.

(1) When the RF changes from OFF to ON, the Active Setpoint remains at the RF-OFF Setpoint for a period specified by ON Delay.

(2) After the ON Delay time has passed, the Active Setpoint is ramped toward the RF-ON Setpoint at a rate specified by Cold Ramp Rate.

(3) After the Active Setpoint has reached the RF-ON Setpoint, changes to the Active Setpoint are done using the Warm Ramp Rate.

(4) Example of a change applied using the faster Warm Ramp Rate.

The front panel contains the following controls and displays:

- RF ON LED

- LIMITED LED

- ERROR LED

- DEE VOLTAGE (digital voltage meter)

- Optical encoder knob

- FINAL pushbutton

- INITIAL pushbutton

- OPEN/CLOSED LOOP toggle switch

- LOCAL/REMOTE toggle switch

- RF ON/OFF (BNC connector)

- RF IN (BNC connector) – to monitor Cavity Voltage

- PEAK DETECTOR IN (BNC connector)

- LIMITER (BNC connector)

- RF OUT (BNC connector)

The RF ON LED indicates the state of the RF.  It is controlled directly by the RF ON/OFF input (i.e. the control logic cannot affect its state).

The LIMITED LED indicates whether or not the LIMITER voltage is within the normal operating range.  It is turned on if the LIMITER voltage exceeds the threshold defined by the Limiter Error parameter.

The ERROR LED indicates that the analog feedback loop is unable to properly regulate the Cavity Voltage.  The control logic monitors the difference between the Active Setpoint and Cavity Voltage and turns on the LED if the difference exceeds the threshold set by the Regulation Error parameter.

The DEE VOLTAGE digital voltage meter normally displays the RF Cavity Voltage.  Whenever the INITIAL or FINAL pushbutton is being pressed, the controller displays the RF-OFF Setpoint or the RF-ON Setpoint, respectively.

The Optical encoder knob is used to change the RF-OFF Setpoint (INITIAL/cold) or RF-ON Setpoint (FINAL/warm) values as follows:

- The RF-OFF Setpoint can be adjusted via the front panel by turning the knob while pressing and holding the INITIAL button.  This operation is independent of the position of the LOCAL/REMOTE switch.

- The RF-ON Setpoint can be adjusted via the front panel by setting the LOCAL/REMOTE switch to the LOCAL position and turning the knob.  NOTE that the meter continues to display the RF Cavity Voltage unless you are also pressing the FINAL button.

The OPEN/CLOSED LOOP toggle switch determines whether or not the analog feedback loop is operational.  In the OPEN position, the feedback loop is disabled and the difference between the Active Setpoint and the Cavity Voltage is not used to regulate the Cavity Voltage.

The RF ON/OFF input enables/disables the RF OUT signal, controls the state of the RF ON LED, and allows the control logic to monitor the ON/OFF state of the RF, which it uses to decide which of the two setpoints the Active Setpoint is ramped toward/set to.

The RF IN input provides the constant RF input signal.  This signal is amplitude modulated by the feedback loop regulation circuit and feed to the RF OUT connector when the RF is ON.  The amplitude of the resulting RF OUT signal ultimately determines the RF Cavity Voltage.

The PEAK DETECTOR IN is used along with the Attenuator switches on the front panel to derive the RF Cavity Voltage.

# Operational Logic

- Real-Time main application process that runs at the highest priority:

  - Handles all application-specific initialization and then runs a continuous loop.

  - The loop is executed every 10ms and runs from start to finish with minimal interruptions

  - At the end of the loop, the process blocks until the start of the next 10ms interval, at which time it is resumed with minimal latency to execute the loop and block again.  The 10ms scheduler timing is quite accurate and is not affected by any delays in the application itself.

  - All values for which the application logic needs to track “single-step” changes (a change between consecutive iterations of the logic loop) are kept in a structure named ApplState.  3 instances of this structure (prev, cur, next) are kept at all times.

  - The loop logic contains the following basic phases:

    - Read the current state of all hardware input signals

    - Update the state of the hardware output signals using “next”

    - Set prev = cur, then cur = next

    - Update values in “cur” using only “prev” and the just-read inputs

    - Update values in “next” using only “prev” and “cur” values

  - Updating the state of the controller takes in to account the following:

    - The current state of the hardware inputs and outputs

    - The current logic state of the controller

    - Requests to change the state of the controller (implied by the current state of the hardware, or received from an external client via a communications channel).

  - Any changes to the desired state of the hardwired output signals are applied at the beginning of the next interval, just after reading the inputs.

The following logic constitutes the logic repeated each pass through the application loop:

- If the INITIAL button is pressed, display the RF-OFF Setpoint on the front panel meter and adjust the RF-OFF Setpoint based on the # of knob-ticks since the last pass.

- If the FINAL button is pressed, display the RF-ON Setpoint on the front panel meter. In addition, if the LOCAL/REMOTE switch is in the LOCAL position, then adjust the RF-ON Setpoint based on the # of knob-ticks since the last pass.

- Update Ramp Mode as follows:

- If the RF is OFF, then Ramp Mode = OFF

- If Ramp Mode = OFF and the RF is ON, then Ramp Mode = WAIT

- If Ramp Mode = WAIT and ON Delay expired, then Ramp Mode = COLD

- If Ramp Mode = COLD and Active Setpoint = RF-ON Setpoint, then Ramp Mode = WARM

- Update Active Setpoint as follows:

- If Ramp Mode = OFF, then Active Setpoint = RF-OFF Setpoint

- If Ramp Mode = WAIT, then Active Setpoint is not changed

- If Ramp Mode = COLD then adjust Active Setpoint toward RF-ON Setpoint using Cold Ramp Rate

- If Ramp Mode = WARM then adjust Active Setpoint toward RF-ON Setpoint using Warm Ramp Rate

- Accept, process, and respond to queries and commands from external sources (typically read via ModBus protocol connections over ethernet).  The commands are typically expressed as changes to values in ModBus registers, and include new values for the configurable parameters and setpoints.

- The ACTIVITY LED is on the rear panel, and is used to check the overall state of the controller.  Normally the LED blinks at approximately 8 Hz.  Slower or varied blink rates may be used to indicate problems or special operating conditions.