Embedded Controller Configuration

Automatic Discovery, Backup, Restore

National Superconducting Cyclotron Laboratory, MSU

## Created:  Mark Davis, 07/26/2006      Last Updated:  Mark Davis, 09/14/2006

### EE Document #: 111-0016-01-01_00.doc

# Introduction

One of the goals of any large, complex control system is to keep maintenance as simple as possible.  As the popularity of devices using embedded controllers continues to rise, their use results in a corresponding rise in the complexity and number of separate devices to be maintained.  Without an effective methodology in place to deal with them, maintenance overhead and reliability will suffer.

At the NSCL, as with most control systems, one of our primary concerns is keeping down-time to a minimum.  When a controller fails, the process of replacing it with a spare must be as simple as possible.  That meant that doing whatever we could to avoid the need for specialized knowledge of the device or use of special configuration software.

As our use of custom (in-house designs) ethernet-based embedded controllers continued to rise, we realized there were 2 main issues that had to be addressed when replacing a controller:  The network configuration had to be set, and any device-specific calibration information had to be loaded.  What we needed was a way to make these happen with as little human interaction as possible.

After debating various approaches, we decided on a simple method that could be applied to all our in-house designs:  The control system database would include a unique id for each active controller, and the id for any given controller could be set to match via switches on the controller.  With this in place, swapping a controller requires only the correct switch settings, and the problem became one of designing software that could automatically locate, monitor, and configure controllers based on these unique ids.

Knowing that humans make mistakes (such as forgetting to set the device ID switches), and that hardware can malfunction (e.g. a failure in the ports connected to the ID switches), it is not enough to simply deal with properly working controllers with the correct switch settings.  The process must also quickly and reliably detect problems, deal with them in a sensible fashion, and alert operators.

The 1st generation of a software design to address these issues fell short of our goals, particularly in terms of being quick to respond to changes and dealing with problems in an appropriate fashion.

This paper describes a 2nd generation design to manage this process.  It is our belief that this newer design will respond much more quickly to changes, as well as providing a much more robust mechanism for detecting and dealing with problems.

# Overview of components

The control system consists of 3 main classes of computing devices:

IOC’s (Input/Output Controllers):

IOC’s are server computers that communicate directly with controllers and/or devices via I/O connections.  Their primary functions are as follows:

  - Monitor the state of controllers and send them commands

  - Aggregate connections from clients (usually workstations) that need to monitor /alter the state of the control system.  This minimizes the # of connections an embedded controller needs to service directly.

  - Implement higher-level control system logic.  This usually involves logic that requires knowing the state of multiple devices, but also often provides extensions to or interpretation of what the controller provides (particularly useful if the controller is from a 3rd party, making changes it to impossible or impractical).

Each IOC also provides the following functionality for the newer automatic configuration process:

- Maintain a list of controllers it is responsible for and the last known state of each.

- Send configuration commands via UDP broadcast packets to controllers that are not responding or have incorrect configurations.

- Monitor all UDP broadcast packets going to or coming from controllers.  Checking ALL the packets allows an IOC to keep an up-to-date picture of the state of all the controllers it is responsible for, as well as detect and respond to situations that might affect the ones it is responsible for (such as a controller using the wrong address, or another IOC sending conflicting configuration commands).

- Remote access to files in a specific directory via a simple TCP protocol.  Used by controllers to archive (and occasionally retrieve) files containing configuration data.  (NOTE:  This service may be provided by one or more servers other than the IOC responsible for a particular controller).

Embedded Controllers:

Embedded controllers generally consist of a small, Single Board Computer (SBC) with a CPU, some memory, and various input/output connections.  The SBC is usually mounted in a larger container and connected directly to supporting circuitry that interfaces with one or more devices to be monitored and controlled.  The following describes the functionality of the newer controllers being designed and built at the NSCL with respect to the automatic configuration process.

- Each controller has a Device Type and a Device ID.  The combination of the Device Type (hard-coded in the firmware) and the Device ID (read from switches mounted in the controller or on the SBC within the controller) must be unique.

- Each controller periodically sends out a broadcast packet announcing its presence and its configuration.  These packets contain the following:

  - The Device Type (hard-coded in firmware)

  - The Device ID (read from switches)

  - The MAC address (static value stored in flash, assigned by the manufacturer)

  - The IP address (configurable via software)

  - The Network mask (configurable via software)

  - The Gateway (configurable via software)

  - The controller name (configurable via software)

  - UpTime (# of seconds since last rebooted)

  - Conflict timestamps (time of various conflicts, if any, the controller detected)

- Configuration data is organized as groups of “persistent” values, and each group has an associated file name.  Any changes to values in a group are periodically saved to the file.  Each group also has an associated category, where the category specifies what the data pertains to.  The 3 possible categories are:

  - SBC-specific.  The most common example is calibration data for the A/D and D/A circuits on a specific SBC (Single Board Computer).

  - Controller-specific.  The most common example is calibration data for analog circuits inside the controller (like the “front end” boards in our BCMs).

  - Device-specific.  The most common example is gain and offsets used to convert analog readings from the device to engineering units (such as converting a voltage read from a potentiometer into a position value in inches or millimeters, or the voltage across a power supply shunt in to amps).  Another example might be names or descriptions of the input/output signals.

Two copies are kept of the current state of each group of configuration values:  One in a local file (stored in flash), and one in a remote file (accessed via a TCP-based simple remote file system protocol).  A limited # of older copies of the files are also kept on the remote file system.

Storing a copy of each configuration data file on a remote server, and associating a category with each one, allows a swapped-in controller to quickly reconfigure itself for a specific device by using the remote copy of the Device-specific data saved by the controller it replaced.

Keeping older copies of the files allows an older configuration to be manually restored if needed.

Workstations:

Workstations provide the human-level interface to the control system.  GUI-based applications running on the workstations communicate primarily with the IOC’s to provide information about the state of the system and allow a person to send commands to the control system.

While communication with individual controllers is often possible, such direct communication is generally limited to diagnostic and testing functions, as doing so often bypasses the higher-level logic in the IOC’s and can overburden the controllers.

Of particular interest to the context of this paper is an application called the Device Manager.  This application allows a person to easily monitor and manage an individual controller or a group of controllers manually.  It is an important diagnostic and testing tool for embedded controllers.

# The Process

Both the control system servers and the controllers maintain a table of timestamps that keep track of when various events last occurred.  These timestamps are regularly updated by monitoring the packets sent to and from controllers.  In addition to keeping track of configuration conflicts, the servers keep track of when a controller was registered with the service, and when the controller was last active.

Each entry includes a timestamp, an IP address, and a MAC address.  Each time a packet is received that indicates a conflict exists, the time the packet was received, the IP address and the MAC address it came from are saved in the appropriate entry in the table.

The possible conflicts are:  Device Type + Device ID, IP Address, and Name.  The table contains two entries for each type, one indicating a conflict between controllers, the other indicating a conflict in the control system configuration.

IOC’s (Input/Output Controllers):

- A configuration process server runs continuously on each IOC that communicates with the controllers over ethernet.  It provides the following functionality:

- Keep a list of all the controllers the IOC is responsible for.  Each entry includes the configuration the controller should have and the last known state of each one (including the event data described above).

- Periodically send out broadcast configuration packets for controllers that are not responding, are incorrectly configured, or are part of a conflict.

- Listen for and process all broadcast packets to or from the controllers.  Each packet will fall in to one of the following categories:

Announcement Packets (sent by a controller):

  - The MAC matches the MAC in one or more conflict events:

    - If the conflict no longer applies, then clear the event data

  - If the controller (Device Type + Device ID) is NOT in our list:

    - The IP Address or Name matches one of the devices in our list:

      - Update the event data for the conflicting value

      - Send a configuration packet to change the conflicting value to a default, non-conflicting value

  - The (Device Type + Device ID) IS in our list:

    - If the Name or IP address is incorrect:

      - If the last-active event timestamp is not set or the MAC address for the last-active event matches:

        - Send a the correct configuration to the controller

        - Update the last-active event data

      - Else

        - Update the data for the controller ID conflict event

        - If the IP address or Name match, update the data for those conflict events as well

    - Else

      - If the last-active event timestamp is not set or the MAC addresses for the last-active event matches:

        - Update the last-active event data

      - Else

        - Update the data for the controller ID, IP Address, and Name conflict events

Command Packets (sent to controllers):

  - The command is for a controller that is not in our list.  No action needs to be taken.

  - The command is for a controller in our list and the configuration matches the one in our list.  No action needs to be taken (although the time such a packet was last detected should be recorded for use in diagnostic commands).

  - The command is for a controller in our list and the configuration does NOT match the one in our list:  Set a status bit indicating a conflict exists in the configuration of the control system (i.e. another IOC is trying to reconfigure one of our controllers using a configuration that does not match the one we have).

- Periodically check the age of each event.  For each one whose age has exceeded some set interval, clear the timestamp and any related data (e.g. if the last active timestamp is being cleared, then clear the MAC address as well).

- Food for thought:  Periodically send command packets to all devices that the servers found are part of a conflict.  The packets would simply instruct the controller to reduce its interval for announcing its configuration so the status of the conflict problem would be updated more quickly.

- A simple remote file system server runs on one or more control system computers and provides basic file system services (create, open, read, write, status, close, delete) to controllers via a TCP connection.  The service is very simplistic and is not secure, so access is usually limited to a specific directory.  Controllers use this service to maintain backup copies of their configuration files.

- The number and age “spread” of the remote backup copies of controller files will be governed by a logarithmic curve that results in a small percentage of older files and a higher percentage of more recent files.  An upper limit on the total # of copies kept for each file will insure the number of archive copies does not grow too large.

Embedded Controllers:

- Periodically read the Device ID from the ID switches.

- Start Controller Configuration daemon (configd).  This process does the following:

- Periodically send out a broadcast packet announcing the controller’s configuration and status.  The packet includes: Device Type, Device ID, IP address, MAC address, Name, seconds since startup, and the conflict-timestamps.

- Listen for and process all broadcast packets to or from other controllers.  Each packet will fall in to one of the following categories:

Announcement Packets (sent by another controller):

  - No conflict (the Device Type + Device ID, the IP address, and the Name are all different).   No action is taken.

  - A conflict exists (the Device Type + Device ID, the IP address, or the Name match).  Update the corresponding conflict-timestamp(s) and reduce the time interval between announcement packets to the minimum.

Command Packets (sent to controllers):

  - The packet is for us (the Device Type + Device ID match).  If the IP Address or the Name is different, update the configuration and reset any timestamp for the conflict type corresponding to the new value(s) (e.g. if the IP Address is different, reset the timestamp for the IP Address conflict).  In any case, reduce the time interval between announcement packets to the minimum (so the sender will be able to quickly determine that the command was received, and any conflicts will show up quickly).

  - The packet is not for us (the Device Type or Device ID is different), but the IP Address or the Name matches ours.  Update the corresponding conflict-timestamp(s) and reduce the time interval between announcement packets to the minimum.

- When first started, whenever a conflict is seen, or the controller’s configuration is changed, the interval between sending the announcement packets is small (around 5 seconds?).   For each interval in which no conflict was seen, the interval is increased (up to some maximum).  To help spread out the timing of packets from the controllers (thereby reducing the risk of broadcast storms and lost packets), the interval will be offset from the standard values used for all controllers by an amount based on its MAC address.

- The date/time of each of the configuration files in flash is periodically compared to the copy kept on the remote server.  If the local copy is newer (or no copy exists on the remote server), then the remote copy is renamed (to archive it) and a new copy is written.

Misc notes, rambling thoughts, work in progress….

The model I use should allow any # of configuration servers (e.g. a master one or one per IOC).

Keep in mind that having a record register itself once with a configuration server when it starts up is not necessarily sufficient.  If the server process dies for some reason, then the list of controllers will be lost.  Conversely, if the EPICS configuration is changed for an IOC, the server process needs to know about that as well.

Because record processing cannot be allowed to block, the record code must be able to call a registration function that does not block, regardless of the state of the configuration server process.

In the EPICS model, there is one thread that processes all the records, and all processes share a global variable space, so I could do pretty much what I do now:  Keep the table of controllers in shared memory and use a mutex to block the configuration process whenever a record is accessing it.  The function could also check to see if there IS a configuration process and, if not, start one.

The process run on the IOC’s could be, for now, the actual configuration server process, or it could be a process that communicates with another process (which could be on another computer) that handles the actual configuration logic.

Outdated configuration data isn’t necessarily a problem.  What’s important is that conflicts are detected and dealt with properly.

Consider this scenario:

A record initializes and registers a controller configuration with the configuration service.  Each time the record is processed, it “refreshes” the configuration with the service (using a handle to make locating the entry quick). The service keeps track of how old each entry is. Rather than automatically deleting entries that are too old (putting a ceiling on how long a record can be idle), this info could be used only when a conflict is detected.

For example:  A controller sends a config-announce packet to announce its configuration, and multiple configuration servers see that it is for a controller in their list.  If the configuration does not match what they think it should be, they send a config-set packet via broadcast.  The configuration servers also see the config-set packet sent by other controllers.  If one of those packets conflicts with entries in its list, then it will do one of 2 things:  If the packet is for a more recently active record, then it deletes its entry.  If the packet is for a less recently active record, then it sends its own config-set packet (which the other server will see is newer than its own, causing it to delete its conflicting entry).   NOTE that the time associated with each entry must be when the record was last processed (i.e. it has nothing to do with controller activity).

Packets from controllers:

|  | 1 | 2 | 3 |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| idRow >= 0 (ctlr is our responsibility) | N | Y |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ipRow >= 0 (using addr in our list) | N | N |  |  |  |  |  |  |  |  |  |  |  |  |  |
| nameRow >= 0 (using name in our list)) | N | N |  |  |  |  |  |  |  |  |  |  |  |  |  |
| macRow >= 0 (we have seen ctlr before) | N | N |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ipRow == idRow (has correct addr) | - | - |  |  |  |  |  |  |  |  |  |  |  |  |  |
| nameRow == idRow (has correct name) | - | - |  |  |  |  |  |  |  |  |  |  |  |  |  |
| macRow == idRow (were talking to it and ???) | - | - |  |  |  |  |  |  |  |  |  |  |  |  |  |
| list[idRow].mac == 0 (only ctlr known to use this ID yet) | - | - |  |  |  |  |  |  |  |  |  |  |  |  |  |
| list[idRow].time | - | - |  |  |  |  |  |  |  |  |  |  |  |  |  |
| list[nameRow].nameConflict | - | - |  |  |  |  |  |  |  |  |  |  |  |  |  |
| list[ipRow].addrConflict | - | - |  |  |  |  |  |  |  |  |  |  |  |  |  |
| list[idrow].idConflict |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| list[macConflictRow].macConflict (MAC of ctlr causing the conflict) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - | - |  |  |  |  |  |  |  |  |  |  |  |  |  |

Keep separate list of MAC addresses that are causing a conflict.  Each row contains:

- MAC address causing conflict

- Type of conflict (ID, IP, Name)

- Time the conflict was detected

- Index in to list of ctlrs the conflict applies to

NOTE:  There can be more than one row with the same MAC address (i.e. one row per conflict, so if a controller is causing multiple conflicts, then there will be multiple rows.

- Packet unrelated to any of the controllers in our list

- Controller using ID we are responsible for; needs to be configured; no known conflicts:

list[idRow].mac = MAC;  list[idRow].time = now;  Send config packet.

- xx

- xx

- xx

if (idRow >= 0)  { // ctlr using ID we are responsible for

}

else  {  // not one of ours – but check for new and old conflicts

if (macRow >= 0)  //

}