ZWorld RF Servo Software Requirements

## Created:  Mark Davis, 10/03/2005      Last Updated:  Mark Davis, 11/20/2012

# Introduction

The RF Servo controller is part of the NSCL control system and is used to monitor and control the position of assemblies within the cyclotron’s RF system.

Basic functional capabilities:

- Control and monitor a remote DC or Bang-Bang Servo motor

- DC or Bang-Bang mode determined by external jumper

- Remote control and monitoring via ethernet connection

- Local/manual control and monitoring via front-panel LEDs, buttons, switches, and a knob

- Software detection (and optional response to) hardware anomalies (e.g. malfunctioning or incorrectly wired limit switches, physical jams, etc).

- Closed-loop active-feedback control of motor based on one of two external analog inputs:  motor position or RF Phase (PID algorithm used for DC Servo motors)

- Device-related calibration/configuration values stored in the controller, automatically backed up (and restored as needed) by the control system

Configurable parameters:

- Amount of mechanical “slop” (hysteresis) between the motor and the device being moved

- Weights (scaling) for the PID loop (for DC Servo active position-feedback control)

- For DC Servos: Minimum reference/control voltage that reliably produces movement (this is normally set by manually initiating a calibration process)

- Fast/Slow scaling rates applied to Local mode Drive & Position controls

- For Position-feedback mode: # of seconds between acting on a new set point and disabling motor movement (0 means never disabled except for errors)

- For Phase-feedback mode: # of seconds between loss of RF and temporarily resorting to Position-feedback mode using the position of the motor at the time the phase-feedback lock was enabled (the “cold position”)

- For Bang-Bang Servos:  2 dead-band values:  One for each feedback mode.

Values settable at runtime:

- Each of the configurable parameters above

- Phase or Position set-point for active-feedback control

- Enable/disable optional functionality

# Required Operational Logic

- On startup:

  - Position set-point = motor position (averaged over 1 second)

  - Initiate active Position-feedback control of the motor

- Monitor state of analog and digital inputs and make state available to control system

- A Drive Lockout/Brake state is supported that disables all movement of the device.  While in this state, all commands (local and remote) that attempt to change the state of the controller or move the device are disabled (except, of course, the one to release the lockout state).  Any attempt to change this state via the front panel controls will cause ALL the front-panel LED’s to blink.

- Support for 3 command modes:

  - Controller-Local:  All front-panel controls are active and remote changes to set-points are ignored.

  - Motor-Local:  Enabled at a switch-box near the motor, this overrides the controller’s ability to move the motor in any way.

  - Remote:  All remote commands are acted on and the following front-panel controls are ignored:  DRIVE switch, POSITION knob, LOCK button.

- Support for 2 active feedback modes:

  - Position:  This is the default mode of operation, where the set-point specifies a motor position and the control loop tries to achieve and maintain the motor position corresponding to the set-point.

  - Phase:  In this mode, the set-point specifies a phase value.  Normally initiated via front-panel while in Local command mode, in which case the set-point is the value of the phase-feedback (Deltha Phi) signal at the time the lock was initiated.

- For DC Servo motors, a standard PID algorithm is used for active feedback control.  A new set-point resets all the PID factors.

For BB Servo motors, movement commands are asserted as needed for each new set-point and are disabled whenever the feedback value reaches or passes the set-point value.  For the existing set-point, movement commands are asserted again only when the error exceeds the (configurable) dead-band value.  The overshoot/undershoot is monitored for both positive and negative movements and used to improve the accuracy of the Position-feedback mode by adjusting the timing of the move commands (i.e. how far in advance of reaching the set-point should the move command be turned off).

In Position-feedback mode, an idle timeout value can be set that disables all motor movement after a period of no new movement commands.

- Pressing the LOCK button by itself while in Controller-Local mode represents a request to toggle between the Position and Phase feedback modes of operation.  Switching to Position-feedback mode can be done at any time, but switching to Phase-feedback mode requires an active RF OK signal.  Attempting to switch to Phase-feedback mode using the button while the controller is NOT in Controller-Local mode or the RF is off causes the LOCK LED to blink rapidly until the button is released.

- The active Phase-feedback mode works as follows:

  - When activated, the current position of the motor is saved (this is referred to as the “cold position”) and the Phase set-point is set to one of 2 values:

    - If the LOCK button is held for less than 2 seconds before being released, then the set-point in effect the last time the Phase-feedback mode was active is used.

    - If the LOCK button is held for MORE than 2 seconds and then released, the current value of the Delta Phi analog input is used.

  - Loss of the RF signal for an extended period of time (a configurable value) will cause the controller to use active Position-feedback mode, using the “cold position” as the set-point.

  - Momentary loss of the RF signal will cause the controller to temporarily use active Position-feedback mode using the current motor position as the set-point.

  - When the RF signal is restored after a loss, the controller will resume normal active Phase-feedback adjustments to the motor position.

  - While RF is on, the LOCK LED will be on.  Any loss of RF will cause the LED to blink.

  - When deactivated, the controller will return to active Position-feedback mode using the current motor position as the set-point.

- Normally the METER analog output reflects current motor position.  Pressing and holding the SET button by itself changes it so it reflects the current set-point instead.  Releasing the SET button causes the METER output to go back to normal.

- In Controller-Local mode, the +/- DRIVE switch and POSITION knob controls on the front panel can be used to alter the motor position.

If the SET button is NOT being pressed, the controls are used to momentarily alter the reference voltage sent to the servo amplifier (for DC Servos) or activate the + or – drive signal (for BB Servos).  The set-point (for the motor position or the phase angle, depending on which feedback mode is active) will follow the current reading.  This mode provides a tight coupling between the controls and the motor movement (i.e. there is no noticeable lag between engaging/disengaging the control and start/end of motor movement).

If the SET button IS being pressed, the controls directly modify the set-point (motor position or phase angle).  This results in a very loose coupling (i.e. noticeable lag between changes made by the controls and when motor movement starts and ends – very much like using a rubber-band to apply a force).  However, it does allow a specific set-point to be applied via the front panel controls independent of the motor response.

The FAST/SLOW switch causes one of two scaling factors to be applied, resulting in 2 different rates of movement (for DC Servos) or set-point changes.

Attempts to use the drive switch or position knob while the controller is in Remote command mode will cause the DRIVE LED’s to blink rapidly, indicating that the commands are being ignored.

- When the controller is in Motor-Local mode, or the ENABLE/DISABLE switch is in the DISABLE position, the set-point must follow the current feedback value to avoid having the controller re-instate the set-point in effect before either of these states where in effect (invariably causing unwanted motor movement).  Unfortunately, RF BB Servo motor switchboxes do NOT have a motor local switch, so the controller cannot tell the difference between unintentional movement due to drift (that it will attempt to correct) and intentional movement due to use of the switchbox.

For BB Servo motors, the only way to avoid this problem is to set the ENABLE/DISABLE switch on the controller to the DISABLE position before using the switchbox at the motor.

- For DC Servos, the /ENABLE signal on the controller’s rear connector acts as both an input and an output.  It is connected to a digital input so the controller can determine when the amplifier is enabled, either via software or via the remote switchbox near the motor.  It is also connected, via the ENABLE/DISABLE switch on the controller’s front panel, to the digital output used to enable the amplifier via software.  Placing the switch in the DISABLE position disconnects the digital output, providing manual override of software control of the amplifier.
 
For BB Servos, the digital output has no effect on the power going to the motor.  It is entirely up to the software to check the state of the switch and cease all movement commands whenever it is in the DISABLE setting.

One of the effects of this arrangement is that the state of the ENABLE/DISABLE switch cannot be determined if the Amplifier Enable output is NOT active.  For BB Servos, this output has no effect, so it can be left in the active state, allowing the state of the front panel switch to be determined.  But for DC Servos, the software cannot tell when the switch setting changes if it has the amplifier disabled (see the entry for the FAULT LED below for more details).

- The FAULT LED is turned on when there is a problem with the servo amplifier (for DC Servos) or (in most cases) when motor movement has been disabled by the ENABLE/DISABLE switch.  The “in most cases” qualifier is due to the fact that, for DC Servos, when the software has disabled the amplifier, it cannot determine the state of the ENABLE/DISABLE switch, and so there are times when changing the state of the switch will NOT result in the LED turning on and off.

- The LOC/REM button is used to toggle between Controller-Local and Remote command modes.  In Controller-Local mode, the DRIVE switch, POSITION knob, and LOCK buttons are active, and the LOCAL LED is on.  In Remote mode, these controls are inactive, and the LOCAL LED is off.  The 3rd command mode, Motor-Local, is enabled/disabled via a switchbox near the motor, and overrides both the other modes.  While Motor-Local mode is active, the LOCAL LED will blink.  When Motor-Local mode is deactivated, the controller will return to the command mode it was in before Motor-Local mode was activated.

- The + and – DRIVE LED’s are used to indicate motor movement.  The controller continuously monitors short-term changes in the motor position (using averaged values) and the noise level on the motor position read-back.  Whenever the motor movement over the last 500ms exceeds the current level of noise, the appropriate LED is turned on.

Using these LED’s to display actual movement (rather than movement commands from the controller) is done for several reasons:

  - Movement commands do not guarantee movement.  Lighting the LED’s based on commands does not provide an immediate feedback as to whether the device is functioning properly.

  - The LED’s are a simpler/faster method of confirming motor movement than looking at a meter reading.

  - The controller has no means of monitoring drive commands from the switchbox near the motor.

  - LED’s turning on and off are a far more effective means of getting the attention of a human operator than changing values on a meter.

  - The DRIVE LED’s indicate movement regardless of what command mode the controller is in, so an operator can quickly tell if there is movement regardless of what caused the movement.

  - DC Servo’s use a variable control voltage and accurately determining what level of voltage constitutes a drive command is even more prone to error than monitoring motor movement.

- For DC Servos, the RESET button and the Amplifier Reset digital output are both connected to the reset input on the servo amplifier.  This allows the software or the operator to reset the amplifier if there is a problem.

- The Move Plus and Move Minus digital outputs are used to control the movement of a Bang-Bang Servo motor.  There is no way to override the software’s control of these outputs while the controller is connected to the motor.

- The ACTIVITY LED is on the back panel of the controller, and is used to check the overall state of the controller.  Normally the LED blinks at approximately 8 Hz.  When calibrating, the LED blinks at approximately 4 Hz.  If there is a hardware problem, it blinks at approximately 1Hz.

# Optional Operational Logic

The following logic can be enabled/disabled on a per-controller basis:

- If an extended period of time passes during which sufficient force to cause movement was continuously applied, but no significant movement occurred, then a hardware error will be reported to the control system. The error condition is automatically cleared when a new set-point is received 5 or more seconds after the error condition was latched.  For front panel controls, the effect is to disable the Drive switch and Position knobs for 5 seconds.

- The above hardware error condition will flash the FAULT LED and disable all motor movement until cleared.

The purpose of this optional functionality is to detect jammed devices and malfunctioning or incorrectly wired limit switches, thereby limiting potential sources of overload conditions that could damage expensive equipment.

NOTES:

  - The 1st option (recognition and reporting of the error) can be enabled without enabling the 2nd option (disabling motor movement until it is cleared).

  - The time period is a configurable value.

  - The amount of movement considered significant is a configurable value.

  - For BB Servos assertion of either of the drive signals constitutes “sufficient force” for movement.  For DC Servos, the smallest reference/control voltage needed to consistently produce movement can be set to a specific value or determined automatically through a calibration process.  The calibration process is activated by pressing the LOCK and SET buttons while the following conditions are met:

    - RF has been OFF for at least 10 seconds

    - The amplifier is enabled

    - The controller is in Controller-Local mode

    - Neither limit switch is activated

The calibration process consists of gradually increasing the reference/control voltage while monitoring the motor position.  If one of the limit switches is activated during the process, the calibration if aborted.

  - A reversal in the direction of the movement command or dropping below the “sufficient force” threshold resets the start of the time period being monitored.

Inputs and Outputs:

DIGITAL INPUTS:

- LOCK button:  Active low when the LOCK button is pressed..

- SET button:  Active low when the SET button is pressed.

- Plus limit:  Active low when positive limit switch is engaged.

- Minus limit:  Active low when negative limit switch engaged.

- Amplifier Enabled:  Active low when the ENABLE/DISABLE switch is in the ENABLE position AND the digital output Amplifier Enable is low.

- Fast/Slow switch:  Low when FAST/SLOW switch is in SLOW position.

- LOC/REM button:  Low when LOC/REM button is pressed.

- Amplifier Fault:  High when DC Servo amplifier is in a Fault state.

- RF OK:  Active low when an RF signal is present.

- BBS jumper:  Active low when Bang-Bang Servo jumper in place.

- DCS jumper:  Active low when DC Servo jumper in place.

- External Local:  High indicates that the control box near the motor has direct control over motor movement.

DIGITAL OUTPUTS:

- LOCAL LED:  Active low turns on LOCAL LED.

- Drive (+) LED:  Active low turns on (+) Drive LED.

- Drive (-) LED:  Active low turns on (-) Drive LED.

- Amplifier Enable:  Active (low) required to enable the DC Servo amplifier (ENABLE/DISABLE switch must ALSO be in ENABLE position).

- LOCKED LED:  Active low turns on LOCKED LED.

- FAULT LED:  Active low turns on FAULT LED.

- Amplifier Reset:  Pulse low to reset DC Servo amplifier.

- Move Plus:  Low to move BB Servo motor in positive direction.

- Move Minus:  Low to move BB Servo motor in negative direction.

- CPU BUSY LED:  Active low to turn on CPU BUSY LED.

- ACTIVITY LED:  Active low to turn on ACTIVITY LED.

ANALOG INPUTS:

- Motor Position:  Voltage across “follow” pot attached to motor.  Indicates position of the motor.

- Plus/Minus Drive switch:  Aprox +3 V indicates switch in (+) position.  Aprox –3V indicates switch in (-) direction.  Aprox 0 V indicates switch in middle position.

- Delta Phi:  +/- 10V per degree of phase angle.

ANALOG OUTPUTS:

- Drive:  +/- reference voltage connected to the DC Servo amplifier.  Larger voltages produce higher velocity or torque movement.

- Meter:  +/- voltage connected to an external meter for displaying current set-point or motor position.