ZWorld Power Supply Reversing Switch Software Requirements

## Created:  Mark Davis, 09/13/2005      Last Updated:  Mark Davis, 08/06/2007

# Introduction

The Reversing Switch controller is part of the NSCL control system and is used to monitor and control the output level and polarity of the connection between a power supply and a load.

Basic functional capabilities:

- Serial (RS-232 or RS-485) connection to power supply (when supported by P.S.)

- Ethernet connection for control data and diagnostic/maintenance

- External Interlock that can override software and shut off power to the power supply

- Software control over power to the power supply (subject to External Interlock state)

- Monitor outputs via Analog inputs (and Serial connection when available)

- Control power supply via Analog outputs OR Serial connection

- Device-related calibration/configuration values stored in the controller, automatically backed up (and restored as needed) by the control system

Configurable parameters:

- Mode of operation (Analog or Serial)

- Maximum current allowed when switching polarity

- Maximum current and voltage allowed during normal operation

- Offset and Gain values for each reading and setting

- Connect Load delay (min time between turning on power supply and connecting the load)

# Standard Operational Requirements

- Monitor state of External Interlock and make state available to control system.

- Monitor P.S. output-voltage, to-load voltage, and load current via analog inputs.

- If serial connection available, monitor settings/readings in use by the power supply (if corresponding analog and serial-read values differ by a large degree, report an error)

- ON command:  If currently OFF and no Interlock condition:

  - Turn on power supply

  - Wait for Connect Load Delay time to pass

  - If Serial mode:

    - Wait for communication with power supply to be established

    - Send set-point of 0

    - Wait for set-point to be acknowledged

  - Connect load and apply current set-point

- OFF command:

  - Turn off power supply and disconnect load

  - If Analog mode, set control voltage to 0

- New set-point:

  - If polarity of the new setting is different than the current output to the load:

    - Change the power supply’s setting to 0

    - Wait for the output to drop below a specified threshold

    - Change the polarity of the connection to the load

  - Change the power supply’s setting to the new set-point

- External Interlock engaged or Maximum Voltage or Current exceeded:

  - Go to OFF state (presence of Interlock status bit allows control system to distinguish this from normal off state)

  - Control system responsible for sending reset signal to both the controller and the source of external interlocks when requested to clear an interlock state

- CPU Activity LED:  Blink at a given frequency when controller functioning normally

| 16 Bit Controller I/O Map |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment Use: |  |  | ZWorld Power Supply Reversing Switch |  |  |  |  |  |  |
| Analog I/O |  |  |  |  |  |  |  |  |  |
| Name | F/S Voltage |  | Use |  |  |  |  |  |  |
| AI00 | 10.00 |  | Power Supply Output Current (Shunt Voltage) |  |  |  |  |  |  |
| AI01 | 10.00 |  | Load Voltage |  |  |  |  |  |  |
| AI02 | 10.00 |  | Power Supply Voltage |  |  |  |  |  |  |
| AI03 | 10.00 |  | Current readback from External Device |  |  |  |  |  |  |
| *NOTE: Add or remove channels as necessary |  |  |  |  |  |  |  |  |  |
| Name | F/S Voltage |  | Use |  |  |  |  |  |  |
| AO00 | 10.20 |  | Setpoint for Analog control mode |  |  |  |  |  |  |
| AO01 | 10.20 |  | Not Used |  |  |  |  |  |  |
| AO02 |  |  | Not Used |  |  |  |  |  |  |
| AO03 |  |  | Not Used |  |  |  |  |  |  |
| *NOTE: Add or remove channels as necessary |  |  |  |  |  |  |  |  |  |
| Digital I/O |  |  |  |  |  |  |  |  |  |
| Name | F/S Voltage |  | Use |  |  |  |  |  |  |
| DI00 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI01 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI02 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI03 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI04 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI05 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI06 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI07 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI08 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI09 | 3.3V |  | Not Used |  |  |  |  |  |  |
| DI10 | 3.3V |  | External Interlock: 0 = OK, 1 = Interlock |  |  |  |  |  |  |
| DI11 | 3.3V |  | PS ON Feedback: 0 = PS OFF, 1 = PS ON |  |  |  |  |  |  |
| Name | F/S Voltage |  | Use |  |  |  |  |  |  |
| DO00 | 5V |  | Normal Polarity LED: 0 = LED ON, 1 = LED OFF |  |  |  |  |  |  |
| DO01 | 5V |  | Reverse Polarity LED: 0 = LED ON, 1 = LED OFF |  |  |  |  |  |  |
| DO02 | 5V |  |  |  |  |  |  |  |  |
| DO03 | 5V |  |  |  |  |  |  |  |  |
| DO04 | 5V |  |  |  |  |  |  |  |  |
| DO05 | 5V |  |  |  |  |  |  |  |  |
| DO06 | 5V |  |  |  |  |  |  |  |  |
| DO07 | 5V |  | PS ON Command: 0 = PS ON, 1 = PS OFF |  |  |  |  |  |  |
| DO08 | 5V |  | Activity LED: 0 = LED ON, 1 = LED OFF |  |  |  |  |  |  |
| DO09 | 5V |  | Normal Polarity: 0 = NOT Normal Polarity or No Load, 1 = Normal Polarity |  |  |  |  |  |  |
| DO10 | 5V |  | Reverse Polarity: 0 = NOT Reverse Polarity or No Load, 1 = Reverse Polarity |  |  |  |  |  |  |