Zworld K1200 TCPS Controller Software Requirements

## Created:  Mark Davis, 09/13/2005      Last Updated:  Mark Davis,  8/06/2007

# Introduction

The K1200 Trim Coil Power Supply Controller is part of the NSCL control system and is used to monitor and control the output level and polarity of the connection between a power supply and a load. Overall control and monitoring is handled via analog and digital inputs and outputs on an embedded Zworld Single Board Computer (SBC).

A variac and a transistor bank control the output of the power supply. The input to the variac is an AC voltage. The output of the variac is rectified and provides the collector bias voltage to the transistor bank. An analog PI circuit controls the transistor bank, regulating the current output. The emitter output from the transistor bank is connected to a reversing switch, which allows control of the polarity of the output.

The Zworld controls the position of the variac via digital outputs that enable movement in one of two directions. The rectified bias voltage is monitored via an analog input and the position of the variac is altered as needed to maintain the voltage within specified parameters. The setting for the analog PI circuit that regulates the current output is set by one of the Zworld’s analog outputs.

The output of the transistor bank is connected to a shunt and the voltage across the shunt is monitored via an analog input (which also provides the feedback for the analog PI circuit). The polarity of the reversing switch is set via a digital output, and the resulting output voltage is monitored via another analog input.

There are 2 different styles of Trim Coil Power Supplies.  The older types use a motor-driven reversing switch.  The position of the motor is set via a single digital output bit.  The motor moves from one position to the other (Normal to Reverse or Reverse to Normal) based on the digital output. When the motor starts moving, it shuts off the power supply.  The only feedback that we have that the polarity switches have been changed from one state to another is that the power supply is shut off and then turned back on as part of this process.

The other type of supply has SCRs connected to the Normal and Reverse polarity relays, controlled by 2 digital outputs on the ZWorld.  For these supplies, the ZWorld is responsible for changing the state of the polarity switches and turning the supply off and back on.

Drawing 096-0131-01-01_00 provides a block diagram showing how these functional blocks are connected together.

Basic functional capabilities:

- Ethernet connection for control data and diagnostic/maintenance

- External Interlock that can override software and shut off power to the power supply

- Software control over power to the power supply (subject to External Interlock state)

- Monitor outputs via Analog and Digital inputs

- Control power supply via Analog and Digital outputs

- Device-related calibration/configuration values stored in the controller, automatically backed up (and restored as needed) by the control system

Configurable parameters:

- Maximum current allowed when switching polarity

- Maximum current and voltage allowed during normal operation

- Offset and Gain values for each reading and setting

- Load connect delay time (in milliseconds)

- Transistor Bank Setpoint Voltage, Vbias (User Set) (10V nominal)

- Transistor Bank Coasting Voltage, Vcoast (User Set) (0.5V nominal)

- Transistor Bank Deadband Voltage, Vdead (User Set) (2V nominal)

Values settable at runtime:

- Each of the configurable parameters above

- The desired output current

# Standard Operational Requirements

- Monitor state of External Interlock and make state available to control system.

- Monitor P.S. output voltage, rectifier voltage, load current, and transistor bank bias via analog inputs.

- ON command:  If currently OFF and no Interlock condition:

  - Turn on power supply

  - Apply transistor bank bias via variac

  - Apply current set point

- OFF command:

  - Turn off power supply

  - Set current command to 0

  - Set Variac down (assert DO00), turn OFF DO01

- New set point:

  - If polarity of the new setting is different than the current output to the load:

    - Change the current setting to 0

    - Wait for the output current to drop below a specified threshold

    - Change the polarity of the connection to the load

    - Wait for the power supply ON Status to indicate that the power supply is back on

    - Wait until the specified delay time has passed

  - Change the current setting to the new setpoint

- External Interlock engaged or Maximum Voltage or Current exceeded:

  - Go to OFF state (presence of Interlock status bit allows control system to distinguish this from normal off state)

  - On user command, control system responsible for sending reset signal to both the controller and the source of external interlocks when requested to clear an interlock state

- CPU Activity LED:  Blink at a given frequency when controller functioning normally.

- Transistor Bank Bias Loop:

  - If the absolute value of the transistor bank bias voltage, Vbank (AI02), minus the setpoint voltage, Vbias, is greater than or equal to the deadband voltage, Vdead, then begin moving the variac to adjust the bias voltage.

  - When the variac is being moved, if the absolute value of the transistor bank bias voltage, Vbank (AI02), minus the setpoint voltage, Vbias, is less than or equal to the coasting voltage, Vcoast, then stop moving the variac.

| 16 Bit Controller I/O Map |  |  |
| --- | --- | --- |
| Equipment Use: |  | K1200 Trim Coil Power Supply Controller |
| Analog I/O |  |  |
| Name | F/S Voltage | Use |
| AI00 | 10.00 | Shunt Voltage (Power Supply Output Current) (10=400A) |
| AI01 | 10.00 | Power Supply Voltage (-10=55V) |
| AI02 | 10.00 | Transistor Bank Bias (-10=55V) |
| AI03 | 10.00 | Output Voltage (-10=55V) |
| *NOTE: Add or remove channels as necessary |  |  |
| Name | F/S Voltage | Use |
| AO00 | 10.20 | Current Setpoint (-10=400A), Initial State = 0V |
| AO01 |  | Not Used |
| AO02 |  | Not Used |
| AO03 |  | Not Used |
| *NOTE: Add or remove channels as necessary |  |  |
| Digital I/O |  |  |
| Name | F/S Voltage | Use |
| DI00 | 3.3V | Outside Control Power: 0 = Power ON, 1 = Power OFF |
| DI01 | 3.3V | Water Flow: 0 = OK, 1 = BAD |
| DI02 | 3.3V | Temperature: 0 = OK , 1 = BAD |
| DI03 | 3.3V | Transistor Bank Fuses: 0 = OK, 1 = BAD |
| DI04 | 3.3V | Interlocks: 0 = OK< 1 = BAD |
| DI05 | 3.3V | ON/OFF Request feedback: 0 = ON requested, 1 = OFF requested |
| DI06 | 3.3V | Primary Overloads: 0 = OK, 1 = Overload |
| DI07 | 3.3V | Manual/Local OFF: 0 = NOT Pressed, 1 = Pressed |
| DI08 | 3.3V | Not Used |
| DI09 | 3.3V | Not Used |
| DI10 | 3.3V | External Interlocks: 0 = OK, 1 = Interlock |
| DI11 | 3.3V | PS Status: 0 = PS ON, no Interlocks, 1= PS OFF |
| Name | F/S Voltage | Use |
| DO00 | 5V | Variac Up: 0 = Move UP, 1 = do NOT move UP |
| DO01 | 5V | Variac Down: 0 = Move DOWN, 1 = do NOT move DOWN |
| DO02 | 5V | Reset Interlocks: 0 pulse = Reset Interlocks, 1 = Normal |
| DO03 | 5V | Output Polarity: 0 = Normal Polarity, 1 = Reversed (NON-SCR supplies only) |
| DO04 | 5V | Supply ON/OFF request: 0 = ON, 1 = OFF |
| DO05 | 5V | Not Used |
| DO06 | 5V | Not Used |
| DO07 | 5V | Not Used |
| DO08 | 5V | Activity LED |
| DO09 | 5V | Normal Polarity: 0 for Reverse Polarity or no load, 1 for Normal Polarity (SCR supplies only) |
| DO10 | 5V | Reverse Polarity: 0 for Normal Polarity or no load, 1 for Reverse Polarity (SCR supplies only) |